## FW_modbus_profile
RW = read write register
MODBUS PROFILE | [7 empty] | R = read only register
PROD CODE: TBD | [7 empty] | INPUT = input register
FW: 000539215 | [7 empty] | HOLDING = holding register
REV: R1.00 | [7 empty] | PRECISION = decimal points
REG.NAME | REG.ADR. | REG.TYPE | MIN | MAX | ATTRIBUTE | PRECISION | DEFAULT VALUE | DESCRIPTION
REG_MSR | 0 | INPUT | 0 | 11 | R | 0 |  | main status register (BIT0=1 alarm is present, BIT1,2,3 -> 0=run, 1=calibration mode, 2=programming, 3=diagnostic, 4= dosing, 5 standby)
REG_ASR_ALM_Level | 1 | INPUT | 0 | 1 | R | 0 |  | Current status of Level Alarm (0=no alarm, 1= alarm)
REG_ASR_ALM_CircPump | 2 | INPUT | 0 | 1 | R | 0 |  | Current status of Circulating Pump Alarm (0=no alarm, 1= alarm)
REG_ASR_ALM_MeasHi | 3 | INPUT | 0 | 1 | R | 0 |  | Current status of High Measure Alarm (0=no alarm, 1= alarm (measure higher than 9 Ph/measure higher than 900 mV)
REG_ASR_ALM_MeasLo | 4 | INPUT | 0 | 1 | R | 0 |  | Current status of Low Measure Alarm (0=no alarm, 1= alarm (measure lower than 5 Ph/measure lower than 300 mV)
REG_ASR_ALM_OFA1 | 5 | INPUT | 0 | 1 | R | 0 |  | Current status of OFA1 Alarm (0=no alarm OFA1, 1= alarm OFA1)
REG_ASR_ALM_OFA2 | 6 | INPUT | 0 | 1 | R | 0 |  | Current status of OFA2 Alarm (0=no alarm OFA2, 1= alarm OFA2)
REG_ISR_Level | 40 | INPUT | 0 | 1 | R | 0 |  | Input Status Register Level (0 = No level Signal Present , 1= Level Signal Present)
REG_ISR_CircPump | 41 | INPUT | 0 | 1 | R | 0 |  | Input Status Register Circulating Pump (0 = No Circulating Pump Signal, 1= Circulating Pump Signal Present)
REG_OSR_RelayAlarm | 80 | INPUT | 0 | 1 | R | 0 |  | Output Status Register Relay Alarm- Closed if any alarm is present(0= Relay Open,1 = Relay Closed)
REG_OSR_RelayAux | 81 | INPUT | 0 | 1 | R | 0 |  | Output Status Register Relay Aux- Closed if the pump is dosing(0= Relay Open,1 = Relay Closed)
REG_Ph_Measure | 2000 | INPUT | 0 | 1400 | R | 2 |  | Current Ph measure (1400 = 14 pH)
REG_mV_Measure | 2001 | INPUT | -99 | 999 | R | 0 |  | Current mV measure
Temperature Measure | 2002 | INPUT | 0 | 500 | R | 1 |  | Current Temperature Measure (*10) in °C or °F depending on the unit set in HR1000
Flow MeasureHi | 2003 | INPUT | 0 | 0xFFFF | R | 0 |  | Absolute flow rate totalizer (L o m3)- High Part
Flow MeasureLo | 2004 | INPUT | 0 | 0xFFFF | R | 0 |  | Absolute flow rate totalizer (L o m3)- Low Part
REG.NAME | REG.ADR. | REG.TYPE | MIN | MAX | ATTRIBUTE | PRECISION | DEFAULT VALUE | DESCRIPTION
REG_ASR_ALMLatch_Level | 0 | HOLDING | 0 | 1 | RW | 0 | 0 | Latch of Level Alarm Register (0=no alarm raised, 1= at leat 1 alarm raised)
REG_ASR_ALMLatch_CircPump | 1 | HOLDING | 0 | 1 | RW | 0 | 0 | Latch of Circulating Pump Alarm Register (0=no alarm raised, 1= at leat 1 alarm raised)
REG_ASR_ALMLatch_MeasHi | 2 | HOLDING | 0 | 1 | RW | 0 | 0 | Latch of High Measure Alarm Register (0=no alarm raised, 1= at leat 1 alarm raised)
REG_ASR_ALMLatch_MeasLo | 3 | HOLDING | 0 | 1 | RW | 0 | 0 | Latch of Low Measure Alarm Register (0=no alarm raised, 1= at leat 1 alarm raised)
REG_ASR_ALMLatch_OFA1 | 4 | HOLDING | 0 | 1 | RW | 0 | 0 | Latch of OFA1 Alarm Register (0=no alarm raised, 1= at leat 1 alarm raised)
REG_ASR_ALMLatch_OFA2 | 5 | HOLDING | 0 | 1 | RW | 0 | 0 | Latch of OFA2 Alarm (0=no alarm raised, 1= at leat 1 alarm raised)
REG_ASR_ALMLatch_RS485Wdg | 6 | HOLDING | 0 | 1 | RW | 0 |  | Latch of Modbus Watchdog Alarm (0=no alarm raised, 1= at leat 1 alarm raised)
REG_ISR_Level | 40 | INPUT | 0 | 1 | R | 0 |  | Input Status Register Level (0 = No level Signal Present , 1= Level Signal Present)
REG_ISR_CircPump | 41 | INPUT | 0 | 1 | R | 0 |  | Input Status Register Circulating Pump (0 = No Circulating Pump Signal, 1= Circulating Pump Signal Present)
REG_OSR_RelayAlarm | 80 | INPUT | 0 | 1 | R | 0 |  | Output Status Register Relay Alarm- Closed if any alarm is present(0= Relay Open,1 = Relay Closed)
REG_OSR_RelayAux | 81 | INPUT | 0 | 1 | R | 0 |  | Output Status Register Relay Aux- Closed if the pump is dosing(0= Relay Open,1 = Relay Closed)
REG_Man_ID_H | 101 | HOLDING | 0 | 0 | R | 0 |  | not used (set to zero)
REG_Man_ID_L | 102 | HOLDING | 0 | 0 | R | 0 |  | not used (set to zero)
REG_Product_ID_H | 103 | HOLDING | 0 | 0 | R | 0 |  | not used (set to zero)
REG_Product_ID_L | 104 | HOLDING | 0 | 0 | R | 0 |  | not used (set to zero)
REG_HW_Version | 105 | HOLDING | 0 | 0 | R | 0 |  | not used(set to zero)
REG_FW_Version | 106 | HOLDING | 0 | 0 | R | 2 | 100 | 100 = 1.00
REG_Serial_nr_H | 107 | HOLDING | 0 | 0 | R | 0 |  | not used(set to zero)
REG_Serial_nr_L | 108 | HOLDING | 0 | 0 | R | 0 |  | not used(set to zero)
REG_ProductionYYMM | 109 | HOLDING | 0 | 0 | R | 0 |  | not used(set to zero)
REG_WatchDog_Timeout | 110 | HOLDING | 0 | 30000 | RW | 0 | 0 | modbus watchdog timer
REG_WatchDog_Action | 111 | HOLDING | 0 | 3 | RW | 0 | 3 | modbus watchdog action
REG_Wdog_counter | 112 | HOLDING | 0 | 65535 | RW | 0 | 0 | modbus watchdog counter
REG_Wdog_Unit | 113 | HOLDING | 1 | 1 | R | 0 | 1 | modbus watchdog unit (1=seconds)
REG_Seko_Modbus_Ver | 114 | HOLDING | 0 | 65535 | R | 1 | 34 | modbus revision guideline
REG_ModBuss_Address | 200 | HOLDING | 1 | 247 | RW | 0 | 1 | modbus device address (writable only if DOA is enabled)
REG_SN_BYTE01 | 201 | HOLDING | 0 | 65535 | RW | 0 | 0 | device serial number byte 01 (writable only once and if zero. Set to zero in diagnostic procedure)not used (set to zero)
REG_SN_BYTE23 | 202 | HOLDING | 0 | 65535 | RW | 0 | 0 | device serial number byte 23(writable only once and if zero. Set to zero in diagnostic procedure)not used (set to zero)
REG_SN_BYTE45 | 203 | HOLDING | 0 | 65535 | RW | 0 | 0 | device serial number byte 45(writable only once and if zero. Set to zero in diagnostic procedure)not used (set to zero)
REG_FC_Low | 204 | HOLDING | 0 | 65535 | R | 0 | 3A28 | firmware code low part (0000539215 = 8 3A4F --> 3A4F)
REG_FC_High | 205 | HOLDING | 0 | 65535 | R | 0 | 8 | firmware code high part (0000539215 = 8 3A4F --> 8) | a
REG_FW_Revision | 206 | HOLDING | 0 | 65535 | R | 2 | 64 | firmware revision (1.0 --> 1.0 *100 =100 = 0x64 )
REG_ProdCodeByteA | 207 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_ProdCodeByteB | 208 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_ProdCodeByteC | 209 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_ProdCodeByteD | 210 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_ProdCodeByteE | 211 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_ProdCodeByteF | 212 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_ProdCodeByteG | 213 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_ProdCodeByteH | 214 | HOLDING | 0 | 65535 | R | 0 | 0x2020 | product code not used(set to zero)
REG_FwSubRevision | 215 | HOLDING | 0 | 65535 | R | 2 | 100 | 100 = 1.00
Web Connection Status | 216 | HOLDING | 0 | 1 | RW | 0 |  | No WEB Connection = 0, Web Connection Present = 1,
REG_Language | 217 | HOLDING | 0 | 5 | RW | 0 | 0 | 0 = English, 1 = Italian, 2= Spanish, 3 = Deutch, 4 = Francais, 5= Russian
Get_Id_REG | 218 | HOLDING | 0x00 | 0x01 | R | 0 | 0xAA | se = 0xAA MainApp Mode, se = 0x55 Boot Mode
Reboot_REG | 219 | HOLDING | 0x00 | 0x01 | RW | 0 | 0 | SE = 1 il device deve aggiornare i campi desiderati in Flash e resettarsi
Reg_Test_Wifi | 220 | HOLDING | 0x00 | 0x01 | RW | 0 | 0 | If set to 1 durring functional test, test is passed
REG_TemperatureUnit | 1000 | HOLDING | 0 | 1 | R | 0 | 0 | Temperature Unit (0= Celsius; 1= fahrenheit)
REG_pHCalibrationType | 1001 | HOLDING | 0 | 3 | R | 0 | 3 | Probe Calibration Type(0= Reference; 1= Off; 2= 1 Point; 3= 2 Points)
REG_RxCalibrationType | 1002 | HOLDING | 0 | 2 | R | 0 | 2 | Probe Calibration Type(0= Reference; 1= Off; 2= 1 Point)
REG_CalibrationOffsetPH | 1003 | HOLDING | 0 | 65535 | R | 2 | 0 | Probe Calibration Offset
REG_CalibrationSlopePH | 1004 | HOLDING | 0 | 65535 | R | 2 | 5916 | Probe Calibration Slope (Mv/pH)*100
REG_CalibrationOffsetRX | 1005 | HOLDING | 0 | 65535 | R | 2 | 0.0 | Probe Calibration Offset
REG_CalibrationSlopeRX | 1006 | HOLDING | 0 | 65535 | R | 2 | 1.0 | Probe Calibration Slope *100
REG_pHSetpointValue | 1007 | HOLDING | 600 | 800 | RW | 2 | 740 | Setpoint Value(600 = 6 pH)
REG_pHSetpointType | 1008 | HOLDING | 0 | 1 | R | 0 | 1 | Setpoint Type (1= Acid; 0= Alcalyne)
REG_RxSetpointValue | 1009 | HOLDING | 400 | 850 | RW | 0 | 700 | Setpoint Value in Mv
REG_RxSetpointType | 1010 | HOLDING | 0 | 1 | R | 0 | 0 | Setpoint Type (0= Low; 1= High)
REG_CircPumpSetting | 1011 | HOLDING | 0 | 1 | RW | 0 | 0 | Circulating Pump Configuration (0=Disabled, 1= Enabled)
REG_InFreqSetting | 1012 | HOLDING | 0 | 1 | RW | 0 | 0 | Frequency Input Configuration (0=Disabled, 1= Enabled)
REG_pH_MeasLow | 1013 | HOLDING | 600 | 600 | R | 2 | 600 (0x258) | Low pH Measure Alarm Treshold (600 = 6,00 pH)
REG_pH_MeasHi | 1014 | HOLDING | 800 | 800 | R | 2 | 800 (0x320) | High pH Measure Alarm Treshold (800 = 8,00 pH)
REG_mV_MeasLow | 1015 | HOLDING | 600 | 800 | R | 0 | 600 (0x258) | Low mV Measure Alarm Treshold (600 = 600 mV)
REG_mV_MeasHi | 1016 | HOLDING | 600 | 800 | R | 0 | 800 (0x320) | High mV Measure Alarm Treshold (800 = 800 mV)
REG_TempLow | 1017 | HOLDING | 100-500 | 100-500 | R | 1 | 100-500 | Low Temperature Alarm Treshold*10 (100= 10 °C 500= 50 °F ) depending on the unit set in HR1000
REG_TempHi | 1018 | HOLDING | 380-1004 | 380-1004 | R | 1 | 380-1004 | High Temperature Alarm Treshold*10 (380= 38 °C 1004= 100,4 °F ) depending on the unit set in HR1000
Produt ID PoolMatch | 1126 | HOLDING | 0 | 4 | R | 0 | NO INIT ONLY VAGNER | Id value that identify PoolMatch: is fix value set at 4
REG_Ph_Measure | 2000 | HOLDING | 0 | 1400 | R | 2 |  | Current Ph measure (1400 = 14 pH)
REG_mV_Measure | 2001 | HOLDING | -99 | 999 | R | 0 |  | Current mV measure
Temperature Measure | 2002 | HOLDING | 0-32 | 550-1310 | R | 1 |  | Current Temperature Measure (*10) in °C or °F depending on the unit set in HR1000
Device Type | 2003 | HOLDING | 0 | 1 | R | 0 | 0 | Redox = 1. Ph = 0;
OFA TIME | 2004 | HOLDING | 0 | 60 | R | 0 | 0 | Programmed OFA Time in minutes (if = 0 OFA is OFF)
FlowRate Unit | 2005 | HOLDING | 0 | 1 | RW | 0 | 1 | m3 = 0, L= 1;
TIME On | 2006 | HOLDING | 1 | 360 | RW | 0 | 30 | Programmed TON Time in seconds
TIME Off | 2007 | HOLDING | 1 | 360 | RW | 0 | 60 | Programmed TOFF Time in seconds
Dosing Type | 2008 | HOLDING | 0 | 3 | R | 0 | 1 | Off = 0, Proportional = 1, On/Off = 2, Timed = 3
Status_REG | 3000 | HOLDING | 0x00 | 0xFFFF | R | 0 |  | Vedi Foglio Status_REG
Standby_REG | 3001 | HOLDING | 0x00 | 0x01 | RW | 0 | 0 | se =1 Pump in Standby Mode, se = 0 Pump in Normal Operation Mode

## Status_REG
n | Item | pH single pump | ORP single pump | pH+ORP double pump | pH+CL+ORP double pump | Green* | Red | Technical Service | Action to do… | WEB APP Message | Accessory product
1 | Temp. Measure <10°C | x | x | x | x |  | x |  | Warninng Cold Water | Poolwater too cold! | Temperature probe
2 | Temp. Measure >38°C | x | x | x | x |  | x |  | Warninng Hot Water | Poolwater too Hot! | Temperature probe
3 | Tank Level Low (pH) | x |  | x | x |  |  | x | Call Technical Service | The chemical is finisced | Level Probe
4 | Tank Level Low (CL) |  | x | x | x |  |  | x | Call Technical Service | The chemical is finisced | Level Probe
5 | pH Measure too low (<6pH) | x |  | x | x |  |  | x | Call Technical Service | pH concentration is to low | ---
6 | pH Measure too High (>8pH) | x |  | x | x |  |  | x | Call Technical Service | pH concentration is to High | ---
7 | ORP Measure too low (<600 mV) |  | x | x | x |  |  | x | Call Technical Service | Chlorine concentration is to low | ---
8 | ORP Measure too High (>800 mV) |  | x | x | x |  |  | x | Call Technical Service | Chlorine concentration is to High | ---
9 | CL Measure too low (<0,30 ppm) |  |  |  | x |  |  | x | Call Technical Service | Chlorine concentration is to low | ---
10 | CL Measure too High (>3 ppm) |  |  |  | x |  |  | x | Call Technical Service | Chlorine concentration is to High | ---
11 | Filtration pump OFF | x | x | x | x |  |  | x | Call Technical Service | The circulation pump is Power OFF | ---
12 | Flowrate Alarm (probe holder reed) | x | x | x | x |  |  | x | Call Technical Service | The circulation pump is Power OFF | Probe Holder with flow check
13 | Standby Status | x | x | x | x |  |  | x |  | =1 Standby Mode, = 0 Normal Operation Mode | ---
14 | OFA pH Time Exprired | x |  | x | x |  | x |  | Reset time dosing By start/stop fuctions | Please reset time out dosing by start/stop remote | ---
15 | OFA ORP Time Exprired |  | x | x | x |  | x |  | Reset time dosing By start/stop fuctions | Please reset time out dosing by start/stop remote | ---
16 | OFA CL Time Exprired |  |  |  | x |  | x |  | Reset time dosing By start/stop fuctions | Please reset time out dosing by start/stop remote | ---
(* Lo stato della Applicazione è sempre verde tranne per i 16 errrori sopra inidicati)